Restrictions – Cameras

Here are some other constraints and things to know about security cameras.

Installation time – Standard protect-IP

| Device | Technician time | Programmer time |
| --- | --- | --- |
| Indoor camera – 1 lens | 1.5 | 1 |
| Indoor camera – 2 lenses | 1.5 | 2 |
| Indoor camera – 3 indoor lenses | 2 | 2.5 |
| Indoor camera - 4 indoor lenses | 2 | 3 |
| Indoor camera - 4 lenses with PTZ | 2 | 4 |
| Outdoor camera – 1 lens | 2.5 | 1 |
| Outdoor camera – 2 lenses | 2.5 | 2 |
| Outdoor camera – 3 indoor lenses | 2.5 | 2.5 |
| Outdoor camera - 4 indoor lenses | 2.5 | 3 |
| Outdoor camera - 4 lenses with PTZ | 3 | 4 |
| Installation server | 4 | 8 |
| UPS | 1 |  |
| Network Switch | 1 | .5 |

Project Management Time:

Project management time is calculated based on the total installation time. We add a percentage to the total time.

Basic standard = 15%, and we adjust based on the type of customer or environment

Project Difficulty Level:

In rare cases, we add a level of difficulty to the project that will affect the time for all lines in the quote. Request a percentage

Mounting brackets

Depending on the type of mounting, a series of brackets will be required. (E.g., see https://i-pro.com/selector/accessory/)

- Wall mount

- Pole mount

- Corner mount

- Hanging

- Parapet mount

- Ceiling mount

Switch engineering

Calculate the number of POE switches depending on the number of cameras and servers.   1 port per camera and 2 ports per server or workstation.  Round up to 48-port switches. We will manually adjust the number of switches.

Each camera has a power draw.

- IEEE 802.3af = POE = 13 W per camera

- IEEE 802.3at = POE+ = 26W per camera

- IEEE 802.3bt = POE++ = 60W per camera

Switches have a maximum wattage budget based on the product number. Calculate the total wattage per camera and per switch.

Server size, bandwidth, and storage

We have websites available to perform this calculation. We will keep this calculation manual for now, as it would be too much effort for you in phase 1.

Example of a website for calculating storage for your  referencehttps://www.ionodes.com/citysafe-storage-calculator/

SD cards in cameras.

If we need to install SD cards inside the cameras in case of loss of communication with the server, calculate 45 minutes of programmer time per camera for installation and configuration.

UPS calculation

The UPS load calculation and number is also important.  Therefore, calculate with a load rate of 80%.

Video Management Software (VMS)

We sell several video management systems from multiple manufacturers.

Genetec, Milestone, Exacq.

Genetec Cameras:

| Type | Product number | Max | Price |
| --- | --- | --- | --- |
| Company | GSC-BASE-E | Unlimited | 0 |
| Base | GSC-BASE-S | 50 cameras |  |

Milestone Camera